## Slide 1: Cryo AIP
Current status
Arkadiy Klebaner
November 21, 2012

## Slide 2: Scope
Compressor system
Refrigeration system
Cryogenic storage and inventory management
Muon g-2 cryogenic distribution system
Mu2e cryogenic distribution system
Auxiliary systems

## Slide 3: Compressor system
A0 compressors (four skids)
Each skid consists of the following:
  Two-stage oil injected screw compressor
  300 kW motor
  60 g/s capacity
  Compression from 1 atm to 20 atm
  Slide valve for capacity control
  6 kW oil pump
  Oil cooler heat exchanger
  Aftercooler heat exchanger
  Oil separator
  Oil removal system
  Entire system is contained on a single,
  fabricated steel base skid, oil removal
  on separate skid
Two-stage compound oil flooded
screw compressor Mycom 2016C

## Slide 4
Helically grooved rotors
Mycom 2016C Two-Stage
Compressor system (cont.)

## Slide 5
Four skids
Consists of:
Oil Separator (located on compr skid)
Oil Coalescers (3 stages)
Charcoal Adsorber
  Removes oil vapor
Molecular Sieve
  Removes water vapor
Final Filter
  Contains 1 micron filter element
Oil Removal System

## Slide 6: Refrigeration system
The system consist of four refrigerators (two dedicated refrigerators for each experiment)
Total theoretical capacity is:
2,500 [W] @ 4.5 K
or
16 [g/sec]
(4 x 625 [W] or 4 x 4 [g/sec])

## Slide 7
Heat Exchanger
35 ft. long heat exchanger
Consists of four heat exchangers
housed in a single cryostat
Nitrogen precooling
U-tube connections for high pressure,
low pressure helium and gas
expander

## Slide 8
Refrigerator Valve Box
Connects all refrigerator components
together using u-tubes
Provides positive isolation between
different components by removing
u-tubes
Distributes cryogens to and from load
and includes necessary control valves
Contains 130 liter subcooling dewar

## Slide 9
Expansion Engines
Two engine types
  Liquid “wet” expansion engine
  30K gas “dry” expansion engine
  3 in and 2 in piston sizes
  2 hp and 7.5 hp respectively

## Slide 10
Gas Storage
Two gas storage consists of 30,000 gal nominal capacity storage tanks
Overall length of 66 ft with an outside diameter of 9 ft

## Slide 11: Nitrogen Tank
15,000 gal
MAWP 150 psig
10' outside diameter
30' tall
65,000 # empty

## Slide 12: Functional Requirements
Detailed requirements are listed in the “ Muon Campus Cryogenics: Functional Requirements Specification” document #4248 in DocDb, initial release October 2, 2012
https://beamdocs.fnal.gov/AD-private/DocDB/ShowDocument?docid=4248
The document is agreed upon and signed by both experiments and management

## Slide 13: Key Requirements
Cryogenic loads:
Muon g-2
  Liquefaction load – 1.4 [g/sec]
  Refrigeration load – 300 [W]
  LN2 Shield flow rate – 1.6 [g/sec]
Mu2e
  Liquefaction load – 0.8 [g/sec]
  Refrigeration load – 350 [W]
  LN2 Shield flow rate – 20 [g/sec]

## Slide 14: Key Requirements (cont.)
The Cryogenic System shall support simultaneous steady state operation of both experiments, Muon g-2 and Mu2e. It shall provide for independent operation of the two experiments, including transient modes, e.g. warm-up, cooldown, etc.
It should be possible to connect and/or isolate Mu2e magnets from the transfer line while under cold conditions

## Slide 15: Piping headers
Towards A0

## Slide 16: Refrigerator room

## Slide 17: Refrigerator room (cont)

## Slide 18: Transfer line

## Slide 19: Transfer line (cont)

## Slide 20: Project Plan
Baseline Costs

## Slide 21: Escalation and Contingency
Escalation
  M&S= 2.7% /year
  SWF= 2.7 % /year
Contingency
  Average 25%
  Exception on items similar to the currently procured for other projects. The smallest is 20%

## Slide 22: Funding Profile

## Slide 23: Labor by Categories

## Slide 24: FY 13 M&S
Long lead items procurement
Removing equipment and refurbishing TeV equipment (1 FTE)
E&D (1 FTE)

## Slide 25: FY14 M&S
Installing TeV equipment
Running headers from A0
Connecting to g-2
Cooling down g-2
9 FTE

## Slide 26: FY15
No M&S
Mu2e E&D work (1.5 FTE)
Will need g-2 operational funds

## Slide 27: FY16
Procuring Mu2e transferline components
Refurbishing and installing TeV transferline, expansion box and headers
Refurbishing and installing AP10 bayonet can
2.8 FTE

## Slide 28: FY17
Connecting Mu2e
Cooling down Mu2e
0.8 FTE

## Slide 29
Plant and g-2
g-2 cryo distribution
2017
2015
2014
2013
2016
Compressors
g-2
Mu2e distribution
Mu2e cryo distribution
Mu2e
Refrigerators
g-2
Refurbishment and installation
Procurement and installation
Cooldown
Engineering and design
Timeline

## Slide 30: Milestones

## Slide 31: Thank you